## Rapid Archive Schedule
RAC-4096 | RAC-4112 | RAC-4128 | RAC-4144 | RAC-4160 | RAC-4166 | RAC-4170 | RAC-4176 | RAC-4192 | RAC-4208 | RAC-4224 | RAC-4240 | RAC-4256 | RAC-4272 | RAC-4288 | RAC-4304 | RAC-4311 | RAC-4320 | RAC-4336 | RAC-4352 | RAC-4368 | RAC-4384 | RAC-4400 | RAC-4416 | RAC-4432 | RAC-4448
v3
Space Information |  |  | Network / Equipment Tree Information | [5 empty] | Network Information (MSTP and IP) | [13 empty] | Definitions and Templates |  | Parameters
Site/Building/Floor (Required) | Room Number (Optional) | Leaf Space (e.g. Room) (Required) | Device Name (Required) | Device FQR Reference (Required) | Device Description (Optional) | Equipment Name (Required) | Served By Equipment Name (Optional) | Controller Part # (Optional) | Engine Name (Required) | Trunk Name (Required) | Controller Host Name (Future) | JCI MAC Address | IP Controller Number | ZIGBEE PAN Offset | Instance # (BACoid) | N2Address | DHCP Enabled | IP Address | Subnet Mask | IP Router | ETH-1 (Optional) | ETH-2 (Optional) | Equipment Definition Name | Controller Template Name
Attribute ID
Attribute Type

## Column Descriptions
Rows 1 and 2 New at Release 13 | - Row 1 contains "column codes" that are used by the SCT Import / Merge process to identify the source of data from the RAC Worksheet. - These new "column codes" allow you to insert user defined columns anywhere in the RAC worksheets without effecting the import / merge interactions between a worksheet and the SCT RAC view. - Note that and Export from SCT into a RAC Spreadsheet must be executed into a worksheet that has not been altered (still some discussion on how this workflow should happen - Column 2 contains the version # of the RAC Workbook. Potential Video Link showing ideas for adding columns and working with the RAC Spreadsheet
Group | Column Heading | RAC Use | New Site Process Description and Notes - SCT RAC View in Edit Mode for Import Process from RAC Spreadsheet (Video Link) | Modify Site Process Description and Notes - SCT RAC View without Edit Mode enabled to Export into RAC Spreadsheet (Video Link) | Summary of Changes at SCT 13
Space Information | Site/Building/Floor | Yes | - Enter the Spaces Tree hierarchy that precedes the Leaf Space column to auto create the Spaces Tree. For Example, BE Headquarters/Campus 507/Building 9/Floor 2 creates a four space parent hierarchy of BE Headquarters, Campus 507, Building 9, Floor 2 before the Leaf Space is appended. - Note that the / is used as the delimiter between the Spaces - See the "New Site Examples" worksheet for best practices on setting up Space and Equipment Relationships. | - The basic Site/Building/Floor information could be roughed in as a starting point for the Modify Process. During the Merge Process from the RAC Spreadsheet, the Site / Building / Floor information can be entered into the spreadsheet but it will not be re-created during the merge. | None
| Room Number | Reference Only | - The Room Number is provided as a reference for Room leaf spaces based on information typically found on the mechanical prints during the creation of a new site. - Note: The updated "Facility Menu" Item in SCT allows you to export the complete Spaces Tree into a spreadsheet. The official Space labels can be added in the spreadsheet and merged back into the Spaces Tree. Link to Video Example of Editing Spaces Tree | This column would typically not be used when adding Spaces and Equipment to an existing archive. | New workflow process to re-label Space Names using the Update Object Label feature.
| Leaf Space (e.g. Room) | Yes | - Enter the Leaf Space associated to the Site/Building/Floor hierarchy that is associated to the Equipment being created for the leaf space. - See the "New Site Examples" worksheet for how terminal unit, AHU and plant equipment schedules Space and Equipment relationships are created against the Leaf Space. - Note: The data populated in this column is added to the field contollers description attribute during the creation of a new Site for MUI. - Note: The updated Facility Menu Item in SCT allows you to export all the Space Labels into a spreadsheet. With this new feature, Space labels can be added in the spreadsheet and quickly merged into the Space Tree. This allows you to start a new project with the Mechanical print Room Numbers as the Leaf Space and use the Update Object Labels feature to quickly update all the space names once the end customer has created their official naming strategy. Link to Video Example of Editing Spaces Tree | - During the process of exporting an Engine into the RAC Spreadsheet, all the Space information can be entered and merged back into the Rapid Archive SCT view. | New workflow process to re-label Space Names using the Update Object Label feature.
All Items / Equipment Tree Information | Device Name | Yes | - At Release 13, this entry now creates only the Device Name in the All Items / Network Trees. - A seperate Equipment Name column entry has been added to the RAC spreadsheet so that unique labels can be created for the Devices in the All Items Tree and the Equipment in SCT's Equipment tab and the MUI Equipment Name. - Under the updated Facility Menu Item in SCT, the Update Object Labels feature allows you to export all the Device Labels into a spreadsheet and update any Device Names before a merge of the Device Names is applied. Link to Video Example of Editing Device Labels and Device Desriptions | - At Release 13, the Export function from SCT RAC to the RAC Spreadsheet will poplulate the Device Names. - You can add an Equipment Name in the new column added at Release 13. - Under the updated Facility Menu Item in SCT, the Update Object Labels feature allows you to export all the Device Labels into a spreadsheet and update any Device Names before a merge of the Device Names is applied. Link to Video Example of Editing Device Labels and Device Descriptions | New - the Device and Equipment Name are unique at Release 13
| Device FQR Reference | Yes | - Enter the Controller's FQR as you want it to appear in the SCT and SMP UI and tool tips. - This column populates the Item Reference name with the fully qualified reference in the Rapid Archive Wizard. | - At Release 13, the Export function from SCT RAC to the RAC Spreadsheet will poplulate the Device FQR Reference. | New - this used to say Device and Equipment FQR
| Device Description | Yes | - This column has been added at Release 13 - For new jobs, the RAC process will add Descriptions to the Device. | - This column has been added at Release 13 - The Descriptions from the devices will be exported into the RAC sheet for use as a reference | New at Release 13
| Equipment Name | Yes | - This column has been added at Release 13 - You can now create unique Device Names and Equipment Names during the RAC process. | - This column has been added at Release 13 - You can now create unique Device Names and Equipment Names during the RAC process. | New - the Device and Equipment Name are unique at Release 13
| Served By Equipment Name | Yes (Optional) | - Enter the exact name of the pre-existing equipment that serves downstream equipment (e.g. the equipment name for an AHU serving a VAV Box) - This column populates the Served By relationship in the SCT Rapid Archive Wizard. - This serving equipment name(s) must already be created in the Equipment Tree of the SCT archive or the serving relationship is not created through the Rapid Archive Wizard process. | - Enter the exact name of the pre-existing equipment that serves downstream equipment (e.g. the equipment name for an AHU serving a VAV Box) - This column populates the Served By relationship in the Rapid Archive Wizard. - This serving equipment name(s) must already be created in the Equipment Tree of the SCT archive or the serving relationship is not created through the Rapid Archive Wizard process. | New - Multiple Served by Equipment Names can be entered with a $$ delimiter
| Controller Part # | Reference Only | - The Controller Part # column is provided as a local reference that does not populate any columns in the Rapid Archive Wizard. | - The Controller Part # column is provided as a local reference that does not populate any columns in the Rapid Archive Wizard.
Network Information (MSTP and IP) | Engine Name | Yes | - Enter the parent NAE name exactly as it appears in the All Items Tree in SCT. - The parent NAE to your controller must already be created in the SCT archive before the Rapid Archive Wizard process is run. | - The Engine Name will be exported to the RAC spreadsheet
| Trunk Name | Yes | - Enter the Trunk Name(s) of the integrations under the Engine Names. - The trunk for your controller must already be created in All Items Tree of the SCT Archive under the desired Engine or the integration relationship will not be created through the Rapid Archive Wizard. - For MSTP Trunks, remember to set the Trunk Number in the Hardware Tab of the MSTP Integration when the trunk is initially created. The Rapid Archive Wizard supports both hardware and remote field bus assignments. MSTP trunks will also have their own JCI MAC Address column per device that needs to be populated. - For IP Trunks, you can only create and name one IP integration per engine. IP trunks will also have their own IP Controller Number column per device that needs to be populated. | - The Trunk Name or Names will be exported to the RAC spreadsheet - Note that N2 Integrations are shown in the exported data - When working in the RAC Spreadsheet with the exported data, this column is a good column to filter on when adding data to the other fields. | N2 Integrations are exported
| Controller Host Name (Future) | Reference Only | - The Controller Host Name column is provided as a local reference that does not populate any columns in the Rapid Archive Wizard. | - The Controller Host Name column is provided as a local reference that does not populate any columns in the Rapid Archive Wizard.
| JCI MAC Address | Yes (Unique for MSTP Integrations) | - The JCI MAC Address is the 8 position dip switch setting on the MSTP controllers or the Rotary switch settings on the Release 10 Field Controllers.. - The uniqueness of the MAC addresses per MSTP integration will be validated during the import into the Rapid Archive Wizard. | - The JCI MAC Address is exported to the RAC spreadsheet | At Release 10, all MSTP field controllers use rotary switches to set the JCI MAC address instead of the 8 position dip switch.
| IP Controller Number | Yes (Unique for IP Integrations) | - The Controller Number is the combined value of the rotary switches on the IP Field Controllers - The uniqueness of the Controller Numbers per IP Integration will be validated by the during the import into Rapid Archive Wizard. | - The Controller Number is exported to the RAC spreadsheet
| ZigBee PANs Offset | Reference Only | - The ZigBee PANs Offset column is provided as a local reference column for users configuring a WNC mesh and does not populate any columns in the Rapid Archive Wizard. - The WNC integration is setup as a Remote Field Bus integration | - Since this is a reference field only, nothing is exported into the RAC spreadsheet
| Instance Number (BACoid) | Yes (Optional) | - It is recommended to leave this column blank. During the RAC import process, unique instance numbers will be automatically be created that are unique to the site archive you are working in. - When this column is populated, the RAC import process only validates Instance Number uniqueness for the new devices being added - not against devices that already exist in the archive. - This column populates the Instance Number column in the Rapid Archive Wizard. | - The Instance Number is exported to the RAC spreadsheet
| N2 Address | Yes - Only on Export | - Not used in New Site Creation | - The Export process will add the N2 address for the N2 Integrations | new at Release 13
| DHCP Enabled | Yes (Unique for IP Integrations) | - Enter True or False to enable or disable DHCP for each IP controller. - When set to True, the IP Address, Subnet Mask and IP Router columns column can be left blank. - When set to False, the IP Address, Subnet Mask and IP Router columns in the RAC Spreadsheet must be populated. | - This value is exported to the RAC spreadsheet
| IP Address | Yes (Only when DHCP Enabled = False) | - When DHCP Enabled is set to True, this column can be blank. - When DHCP Enabled is set to False, the IP Address, Subnet Mask and IP Router columns in the RAC Spreadsheet must be populated. | - This value is exported to the RAC spreadsheet
| Subnet Mask | Yes (Only when DHCP Enabled = False) | - When DHCP Enabled is set to True, this column can be blank. - When DHCP Enabled is set to False, the IP Address, Subnet Mask and IP Router columns in the RAC Spreadsheet must be populated. | - This value is exported to the RAC spreadsheet
| IP Router | Yes (Only when DHCP Enabled = False) | - When DHCP Enabled is set to True, this column can be blank. - When DHCP Enabled is set to False, the IP Address, Subnet Mask and IP Router columns in the RAC Spreadsheet must be populated. | - This value is exported to the RAC spreadsheet
| ETH-1 | Reference Only | - The ETH-1 Column is provided as a reference to show how the IP trunk cabling connections are made. If a daisy chain network is created, the ETH-1 and EHT-2 columns can be used to show how the daisy chain was created. | - Since this is a reference field only, nothing is exported into the RAC spreadsheet
| ETH-2 | Reference Only | - The ETH-1 Column is provided as a reference to show how the IP trunk cabling connections are made. If a daisy chain network is created, the ETH-1 and EHT-2 columns can be used to show how the daisy chain was created. | - Since this is a reference field only, nothing is exported into the RAC spreadsheet
Definitions and Templates | Equipment Definition Name | Reference Only in New Site Creation Required when updating existing sites with Spaces and Equipment | - This is an optional / reference field for the new Site Process - The Equipment Definitions must be entered in SCT Equipment Folder and be referenced in a Controller Template prior to executing the Rapid Archive Wizard. The Equipment Definition creates the Equipment Instances in the SCT Equipment tab when the Rapid Archive Wizard is saved. Other Tips - It is recommended that one Equipment Definition be used to create all the Equipment Instances of the same general type. For example, one Single Duct VAV Box Equipment Definition could be created for Single Duct VAV Boxes that are cooling only, cooling with reheat or fan powered. - Under the Facility Menu Item, the new Prepare Rapid Archive process allows you to quickly start the workflow to create a Controller Template from a caf file and build an associated Equipment Definition from the Controller Template - Note that an Equipment Definition can be quickly created from a Controller Template at Release 13 (right cliek menu item on the controller template) | - This is a required field in the RAC Spreadsheet once the export has been made - The Equipment Definitions must be entered in the SCT Equipment Folder before the merge process is initated. | New Workflows to quickly create an Equipment Defintion from a Controller Template Link to future Videos that show the updates to updated workflows
| Controller Template Name | Required in New Site Creation Not Required when updating existing sites with Spaces and Equipment | - This is a required field in the RAC Spreadsheet - The Controller Template also needs to include the reference to the associated Equipment Definition. - Enter the Controller Template name as displayed in the SCT UI. - This column populates the Controller Template column in the SCT Rapid Archive View. - Only Controller Templates with a Equipment Definitions reference will create Equipment Instances. - The Controller Templates for a site's archive need to be defined and added to the archive before the RAC Schedule is imported. - Remember to setup the Point Name Display attributes in the Controller Template to match the desired Point Naming strategy for your site. - The Metasys Field Controllers, the Controller Template should also include the extention to the caf Resource file used to build the points in the Template. Once the RAC Process is run, all the field devices created from the controller template will include a caf resource file that has the Updated Parameters in the columns following the Controller Template Name. | - This field is not used at all in the RAC Spreadsheet during a Modify Site Process | New Workflows to quickly create an Equipment Defintion from a Controller Template Link to future Videos that show the updates to updated workflows
Parameters | See Parameter Worksheet Examples | Yes (Optional) | Example Parameter Sheets are provided as part of this spreadsheet. The example heading data provided in these worksheets can be copied into your master or scratchpad worksheets next to the Controller Template Name column. The examples provided are for VAV Box parameters like Box Areas, k-factors and CFM setpoints. The parameter sheet values can be created from the CCT Trunk Utility Template Files. | The Parameters feature is not used during the Modify Site Process.

## J.R. Instructions
RAC-4096 | RAC-4112 | RAC-4128 | RAC-4144 | RAC-4160 | RAC-4166 | RAC-4170 |  | RAC-4176 |  | RAC-4192 | RAC-4208 | RAC-4224 | RAC-4240 | RAC-4256 | RAC-4272 | RAC-4288 | RAC-4304 | RAC-4311 | RAC-4320 | RAC-4336 | RAC-4352 | RAC-4368 | RAC-4384 | RAC-4400 | RAC-4416 | RAC-4432 |  | RAC-4448
v3
Space Information |  |  | Network / Equipment Tree Information | [7 empty] | Network Information (MSTP and IP) | [13 empty] | Definitions and Templates |  | Sensor | Parameters
Site/Building/Floor (Required) | Room Number (Optional) | Leaf Space (e.g. Room) (Required) | Device Name (Required) | Device FQR Reference (Required) | Device Description (Optional) | Equipment Name (Required) | Mechanical Drawing | Served By Equipment Name (Optional) | JCI Ctrl Dwg No. | Controller Part # (Optional) | Engine Name (Required) | Trunk Name (Required) | Controller Host Name (Future) | JCI MAC Address | IP Controller Number | ZIGBEE PAN Offset | Instance # (BACoid) | N2Address | DHCP Enabled | IP Address | Subnet Mask | IP Router | ETH-1 (Optional) | ETH-2 (Optional) | Equipment Definition Name (Optional) | Controller Template Name (Required) | Code No | Box Heat | Supplemental Heat | Inlet Size (inches) | SA-AREA | SA-KFACTOR | CLG-MAXFLOW | CLGOCC-MINFLOW | HTGOCC-MAXFLOW | HTGOCC-MINFLOW | Comments
|  |  | Attribute ID | [27 empty] | AV3111 | AV3112 | AV3108 | AV3109 |  | AV3110
|  |  | Attribute Type | [27 empty] | Default Value | Default Value | Default Value | Default Value | Default Value | Default Value
Template Instructions - This Template is based v3 of the RAC Schedule Master. When a Master is issued, a new Template should be generated using the new Master. Insert the required columns, update the equations as needed - This Template is setup for Hardware engineering to be a starting place for Software engineering. Some of the fields are specific to Software and have no impact on Hardware but can be used to setup Software for success - The equations for Device Name, Device FQR Reference, and Device Description are based off a specific customer's standard. Adapt the equations as needed to meet the project customer's standards - For information on the functions used, refer to Microsoft Help or O365 training - Comments on each cell help explain the specific use and updating requirements of the information in the cells |  |  |  | 1. Copy the Manufacturer sheet from this workbook to the project RAC Schedule 2. Copy the columns from New Empty Scratchpad which get added to the RAC Schedule and paste them in the proper locations 3. Copy the formulas from this page to the New Empty Scratchpad in the project RAC Schedule. 4. Paste the functions (only the functions) in the first row used for the schedule data. 5. Choose the Manufacturer for the boxes and complete the table as noted below.
Plant Systems | [5 empty] | .
MPL |  | MillRd | MRs-HWS | 031CG004 | MRs-HWS - MillRd | HWS | M3.1 |  | 01.01.01 | M4-CGM04060-0 | S3-SNE03 | FC-1 |  | 4 |  |  | 1003104
Air Systems
MPL/MillRd |  | Floor 1 | MR-AHU-1 | 031CG005 | MR-AHU-1 - Floor 1 | AHU-1 | M2.1 | HWS,CHWS | 02.01.01 | M4-CGM09090-0 | S3-SNE03 | FC-1 |  | 5 |  |  | 1003105
Terminal Systems
MPL/MillRd/Floor 1 | 150A | Public Vestibule | MR-VAV-1 | 031CV006 | MR-VAV-1 - Public Vestibule Rm 150A | VAV-1 | M2.1 | AHU-1, HWS | 03.02.01 | M4-CVM03050-0 | S3-SNE03 | FC-1 |  | 6 |  |  | 1003106 | [7 empty] | VAV | VAV-RH | NSB8BTN245-0 | TRUE | FALSE | 4 | 0.09 | 1.63 | 100 | 100 | 100 | 100
MPL/MillRd/Floor 1 | 150A | Public Vestibule | MR-VAV-1 | 031CV007 | MR-VAV-1 - Public Vestibule Rm 150A | VAV-1 | M2.1 | AHU-1, HWS | 03.02.01 | M4-CVM03050-0 | S3-SNE03 | FC-1 |  | 7 |  |  | 1003107 | [7 empty] | VAV | VAV-CLG | NSB8BTN245-0 | FALSE | FALSE | 8 | 0.35 | 2.39 | 525 | 525
MPL/MillRd/Floor 1 | 150A | Public Vestibule | MR-VAV-1 | 031CV008 | MR-VAV-1 - Public Vestibule Rm 150A | VAV-1 | M2.1 | AHU-1, HWS | 03.02.01 | M4-CVM03050-0 | S3-SNE03 | FC-1 |  | 8 |  |  | 1003108 | [7 empty] | VAV | VAV-RAD | NSB8BTN245-0 | TRUE | TRUE | 4 | 0.09 | 1.63 | 100 | 30 | 65 | 30
MPL/MillRd/Floor 1 | 150A | Public Vestibule | MR-VAV-1 | 031CV009 | MR-VAV-1 - Public Vestibule Rm 150A | VAV-1 | M2.1 | AHU-1, HWS | 03.02.01 | M4-CVM03050-0 | S3-SNE03 | FC-1 |  | 9 |  |  | 1003109 | [7 empty] | VAV | VAV-RAD | NSB8BTN245-0 | TRUE | TRUE | 10 | 0.55 | 2.31 | 700 | 165 | 433 | 165
MPL/MillRd/Floor 1 | 150A | Public Vestibule | MR-VAV-1 | 031CV010 | MR-VAV-1 - Public Vestibule Rm 150A | VAV-1 | M2.1 | AHU-1, HWS | 03.02.01 | M4-CVM03050-0 | S3-SNE03 | FC-1 |  | 10 |  |  | 1003110 | [7 empty] | VAV | VAV-RH | NSB8BTN245-0 | TRUE | FALSE | 6 | 0.2 | 3.07 | 350 | 85 | 218 | 85
Note on D1: J. R. Frost: Hide this column for hardware submittal
Note on E1: J. R. Frost: Hide this column for hardware submittal
Note on N1: J. R. Frost: Hide this column for hardware submittal if not used for this submittal. i.e. if it isn't using BACnetIP controllers, hide the associated columns
Note on O1: J. R. Frost: Hide this column for hardware submittal if not used for this submittal. i.e. if it isn't using MSTP controllers, hide the associated columns
Note on P1: J. R. Frost: Hide this column for hardware submittal if not used for this submittal. i.e. if it isn't using BACnetIP controllers, hide the associated columns
Note on Q1: J. R. Frost: Hide this column for hardware submittal if not used for this submittal. i.e. if it isn't using Wireless controllers, hide the associated columns
Note on R1: J. R. Frost: Hide this column for hardware submittal
Note on S1: J. R. Frost: Hide this column for hardware submittal if not used for this submittal. i.e. if it isn't using N2 controllers, hide the associated columns
Note on T1: J. R. Frost: Hide this column for hardware submittal if not used for this submittal. i.e. if it isn't using BACnetIP controllers, hide the associated columns
Note on U1: J. R. Frost: Hide this column for hardware submittal if not used for this submittal. i.e. if it isn't using BACnetIP controllers, hide the associated columns
Note on V1: J. R. Frost: Hide this column for hardware submittal if not used for this submittal. i.e. if it isn't using BACnetIP controllers, hide the associated columns
Note on W1: J. R. Frost: Hide this column for hardware submittal if not used for this submittal. i.e. if it isn't using BACnetIP controllers, hide the associated columns
Note on X1: J. R. Frost: Hide this column for hardware submittal if not used for this submittal. i.e. if it isn't using BACnetIP controllers, hide the associated columns
Note on Y1: J. R. Frost: Hide this column for hardware submittal if not used for this submittal. i.e. if it isn't using BACnetIP controllers, hide the associated columns
Note on Z1: J. R. Frost: Hide this column for hardware submittal
Note on A9: J. R. Frost: Enter the space information to the last segment. For a building wide system, enter the "Site" and that is all.
Note on C9: J. R. Frost: The "Leaf Space" is the most specific indication of what the system serves. For a building side system, the Leaf Space is the Building Name.
Note on D9: J. R. Frost: CONCAT("MR-",G9) CONCAT is the new name for the function CONCATENATE (can use either function name). The function takes strings from multiple locations and combines them into a single string. This equation is specific to this customer because of how they want their controllers named in the tree. They want their abbreviation for the building combined with the equipment name. To do this, CONTACT the abbreviation with the equipment name. Entering specific text not from a cell requires bracketing the text in quotation marks.
Note on E9: J. R. Frost: CONCAT(RIGHT(L9,2),RIGHT(M9,1),MID(K9,4,2),"0",RIGHT(R9,2)) CONCAT is the new name for the function CONCATENATE (can use either function name). The function takes strings from multiple locations and combines them into a single string. RIGHT is a function which selects the last characters from a string. Designate the location of the string and number of characters. MID is a function with selects characters in the middle of a string. Designate the location of the string, which character in the string to start at, and then how many characters to select. This equation is setup to match this customer's preferred identifier standard for their controllers. It identifies the engine, the bus, the type of controller, and addressing information of the controller. This is based on a modified version of controller identification from the legacy NAE Point Schedule tool which used to be used for database buliding.
Note on F9: J. R. Frost: CONCAT(D9," - ",C9,IF(ISBLANK(B9),"",CONCAT(" Rm ",B9))) IF is a function which evalutes a logical expression and returns 1 of 2 designated responses. ISBLANK is a logical function with indicates if a cell is blank or not This equation is built to combine the Device Name, Service space (Leaf Space) and Room Number (if present). This works well for terminal equipment. For larger systems (plant equipment, air handlers), typically replace the Leaf Space and Room with panel number and location (i.e. "Panel P-2 - Mech Rm 109)
Note on G9: J. R. Frost: Equipment designation from mechanical plans
Note on H9: J. R. Frost: Primary plan page which indicates the physical location of the equipment
Note on I9: J. R. Frost: The list of equipment names which provide service to the equipment. Spelling matters when doing the Software work. For most plant systems, it will be either blank or the specific boiler/chiller/pump integrated devices. For AHUs it will usually be the plant systems which feed the coils.
Note on J9: J. R. Frost: Control drawing page which shows the flow diagram for the system.
Note on K9: J. R. Frost: The part number for the controller. This can be the common part number (i.e. "CGM09090) or actual part number (M4-CGM09090-0).
Note on L9: J. R. Frost: Engine designation. For hardware engineering, this simply needs to reflect the engine name matching the customer's standard. For software engineerig, this has to match character for character of what is in the database
Note on M9: J. R. Frost: Bus designation. Traditionally, this has been a direct reference to the label on the engine or a substitution of FC-1 for FCA
Note on N9: J. R. Frost: Only applicable to BacnetIP controllers and still not incorporated RAC functionality at this point
Note on O9: J. R. Frost: This is the hardware address of the MS/TP controller. This is assigned by the JCI Hardware engineer. Include this information even for non-JCI controllers on the schedule as the instance number is based on this value
Note on P9: J. R. Frost: The equivalent of JCI MAC Address for BACnetIP controllers
Note on Q9: J. R. Frost: Wireless
Note on R9: J. R. Frost: A unique identifying number across the customer network, not simply the bus. To ensure a unique assignment, use the BACnet Tracking List v2.4.xlsm (or current version if they update it) to cover up to 16 buses per engine.
Note on S9: J. R. Frost: N2 address. Typically will on see this on retrofit projects. Use the N2 address of the controller you are replacing. This is sometimes an issue if replacing a VAV or VMA controller with an N2 address over 127
Note on T9: J. R. Frost: BACnetIP
Note on U9: J. R. Frost: BACnetIP
Note on V9: J. R. Frost: BACnetIP
Note on W9: J. R. Frost: BACnetIP
Note on X9: J. R. Frost: BACnetIP if using Daisy Chain or Ring typography
Note on Y9: J. R. Frost: BACnetIP if using Daisy Chain or Ring typography
Note on Z9: J. R. Frost: Match the SCT database
Note on AA9: J. R. Frost: If there is existing, match the SCT database. If it is new, use a designation which reflects the major funtion of the system. i.e. HWS for Hot Water System, AHU-type for AHUs using the same sequencing.
Note on AB9: J. R. Frost: Only applicable to terminal unit control (or an Air System if it serves a single space)
Note on A11: J. R. Frost: Enter the space information to the last segment. For a system which serves an area or floor, enter the "Site" and "Building" and that is all.
Note on C11: J. R. Frost: The "Leaf Space" is the most specific indication of what the system serves. For a system which serves an area or floor, the Leaf Space is the overall area or floor.
Note on A13: J. R. Frost: Enter the space information to the last segment. For a system which serves a space, enter the "Site" and "Building" and "Floor" and not the space.
Note on B13: J. R. Frost: Room Number is applicable to spaces, not to floors or buildings.
Note on C13: J. R. Frost: The "Leaf Space" is the most specific indication of what the system serves. For terminal systems, the Leaf Space is space name.
Note on AC13: J. R. Frost: IF(AND(NOT(ISBLANK(AA9)),NOT(EXACT(AA9,"VAV-CLG"))),TRUE,FALSE) AND is a logical function where all arguments have to be true NOT is a logical function which reverses the output of a logical expression EXACT is a logical function which checks to see if text strings match exactly This equation checks the value in Controller Template Name to check if a terminal system has reheat or not
Note on AD13: J. R. Frost: IF(EXACT(AA13,"VAV-RAD"),TRUE,FALSE) The equation checks to see if the name in Controller Template Name indicates the terminal system has radiant heating associated with it or not.
Note on AE13: J. R. Frost: Box inlet diameter from the equipment submittal
Note on AF13: J. R. Frost: VLOOKUP($AE13,Manufacturer!$B$2:$E$22,3) VLOOKUP is a function which looks for a specifc value in the first column of a table (or array) and returns the value in a specified column of that table on that row For this equation to work properly when copied to other rows or colunmns, the column reference of the first arguement has to be locked (as above) and the table reference has to be locked (as above) to ensure the value it looks for doesn't change from the "Inlet Size". This equation look on the Manufacturer's tab to return the area entered for the associated box size. Change the Manufactuter in the drop down on that sheet to update the table. This prevents the need to edit/adapt the functions as entered once the Manufacturer sheet is copied to the project RAC schedule.
Note on AG13: J. R. Frost: VLOOKUP($AE13,Manufacturer!$B$2:$E$22,4) This equation look on the Area & K-Factors tab to return the flow gain entered for the associated box size. Change the Manufactuter in the drop down on that sheet to update the table. This prevents the need to edit/adapt the functions as entered once the Manufacturer sheet is copied to the project RAC schedule.
Note on AH13: J. R. Frost: Flow SP from the equipment submittal
Note on AI13: J. R. Frost: Flow SP from the equipment submittal
Note on AJ13: J. R. Frost: Only applicable if the sequence calls for a reset of air flow in heating mode.
Note on AK13: J. R. Frost: Flow SP from the equipment submittal

## Manufacturer
[19 empty] | Anemostat |  |  | 5 | 6
| Titus |  | 31 | 32 | [14 empty] | Carnes Cross-Flow |  |  | 9 | 10
| If you have an unknown manufacture, or the manufacturre is not listed in this sheet, use the K Factors below. | [17 empty] | Carnes Standard |  |  | 7 | 8
VAV Box Duct Size | Area | Average K Factor | [16 empty] | Carrier |  |  | 11 | 12
4 | 0.09 | 1.63 | [16 empty] | EH Price |  |  | 13 | 14
5 | 0.14 | 1.95 | [16 empty] | Enviromental Tech 45 (Largo) |  |  | 15 | 16
6 | 0.2 | 3.07 | [16 empty] | Enviromental Tech 90 (Largo) |  |  | 17 | 18
7 | 0.27 | 2.57 | [16 empty] | Generic (Unknown) |  |  | 3 | 4
8 | 0.35 | 2.39 | [16 empty] | Krueger |  |  | 19 | 20
9 | 0.44 | 2.3 | [16 empty] | Metal Industries |  |  | 21 | 22
10 | 0.55 | 2.31 | [16 empty] | Nailor |  |  | 23 | 24
12 | 0.79 | 2.76 | [16 empty] | Redd-i |  |  | 25 | 26
14 | 1.07 | 2.02 | [16 empty] | Temperature Industries |  |  | 27 | 28
16 | 1.4 | 1.12 | [16 empty] | Tempmaster (York) |  |  | 29 | 30
18 | n/a | n/a | [16 empty] | Titus |  |  | 31 | 32
19 | n/a | n/a | [16 empty] | Tuttle and Bailey |  |  | 33 | 34
20 | 0.78 | 2.19 | [16 empty] | VariTrane F-Style |  |  | 35 | 36
22 | 0.78 | 2.19
24 | n/a | n/a
26 | 1 | 2.57
30 | n/a | n/a
40 | 2.67 | 2.22
| 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33 | 34 | 35 | 36
| Generic If you have an unknown manufacture, or the manufacturre is not listed in this sheet, use the K Factors below. |  | Anemostat |  | Carnes Standard |  | Carnes Cross-Flow |  | Carrier |  | EH Price SD/FP/DD Inlet Boxes |  | Environmental Tech. 45 deg travel (Largo) |  | EnviroTech 90deg Travel (Largo) |  | Krueger |  | Metal Industries |  | Nailor |  | Redd-i |  | Temperature Industries |  | Tempmaster (York) |  | Titus |  | Tuttle and Bailey |  | VariTrane F-Style Boxes
VAV Box Duct Size
| Area | K Factor | Area | K Factor | Area | K Factor | Area | K Factor | Area | K Factor | Area | K Factor | Area | K Factor | Area | K Factor | Area | K Factor | Area | K Factor | Area | K Factor | Area | K Factor | Area | K Factor | Area | K Factor | Area | K Factor | Area | K Factor | Area | K Factor
4 | 0.087266 | 1.9956 | n/a | n/a | n/a | n/a | n/a | n/a | 0.09 | 2.26 | 0.09 | 1 | 0.09 | 1.71 | 0.08 | 1.63 | 0.09 | 2.32 | n/a | n/a | 0.09 | 2.92 | n/a | n/a | n/a | n/a | n/a | n/a | 0.09 | 1.63 | 0.09 | 2.8 | 0.09 | 1.69
5 | 0.13635 | 2.1564 | 0.13 | 3.28 | 0.13 | 2.42 | 0.13 | 2.42 | 0.14 | 2.26 | 0.14 | 1.47 | 0.14 | 1.69 | 0.13 | 1.66 | 0.14 | 2.31 | n/a | n/a | 0.14 | 2.99 | n/a | n/a | 0.14 | 1.62 | 0.14 | 1.62 | 0.14 | 1.95 | 0.14 | 3 | 0.14 | 1.5
6 | 0.19635 | 2.3919 | 0.19 | 2.58 | 0.19 | 2.37 | 0.19 | 2.37 | 0.2 | 2.45 | 0.2 | 2.8 | 0.2 | 1.67 | 0.18 | 2.9 | 0.2 | 2.32 | 0.18 | 1.5 | 0.2 | 3.08 | 0.2 | 2.39 | 0.2 | 1.78 | 0.2 | 1.78 | 0.2 | 3.07 | 0.2 | 2.9 | 0.2 | 2.31
7 | 0.26725 | 2.3855 | 0.26 | 2.85 | 0.26 | 2.4 | 0.26 | 2.4 | 0.27 | 2.27 | 0.27 | 2.34 | n/a | n/a | n/a | n/a | 0.27 | 2.32 | n/a | n/a | 0.27 | 2.85 | n/a | n/a | 0.27 | 1.62 | 0.27 | 1.62 | 0.27 | 2.57 | 0.27 | 3 | n/a | n/a
8 | 0.34907 | 2.1875 | 0.34 | 2.44 | 0.34 | 2.2 | 0.34 | 2.2 | 0.35 | 2.27 | 0.35 | 2.24 | 0.35 | 1.61 | 0.33 | 2.52 | 0.35 | 2.33 | 0.33 | 1.46 | 0.35 | 2.65 | 0.35 | 2.89 | 0.35 | 1.36 | 0.35 | 1.36 | 0.35 | 2.39 | 0.35 | 2.9 | 0.35 | 2.18
9 | 0.44179 | 2.3 | 0.43 | 2.46 | n/a | n/a | n/a | n/a | 0.44 | 2.27 | 0.44 | 2.21 | n/a | n/a | n/a | n/a | 0.44 | 2.33 | n/a | n/a | 0.44 | 2.23 | n/a | n/a | n/a | n/a | n/a | n/a | 0.44 | 2.3 | n/a | n/a | n/a | n/a
10 | 0.54542 | 2.1825 | 0.53 | 2.48 | 0.53 | 2.1 | 0.53 | 2.1 | 0.55 | 2.27 | 0.55 | 1.96 | 0.52 | 1.63 | 0.53 | 2.41 | 0.55 | 2.32 | 0.52 | 1.52 | 0.55 | 2.42 | 0.55 | 2.98 | 0.55 | 1.68 | 0.55 | 1.68 | 0.55 | 2.31 | 0.55 | 3 | 0.55 | 2.06
12 | 0.7854 | 2.3638 | 0.77 | 2.92 | 0.77 | 2 | 0.77 | 2 | 0.79 | 2.27 | 0.79 | 2.03 | 0.69 | 1.61 | 0.76 | 2.38 | 0.79 | 2.32 | 0.76 | 1.48 | 0.79 | 2.52 | 0.79 | 2.79 | 0.79 | 2.77 | 0.79 | 2.77 | 0.79 | 2.76 | 0.79 | 3 | 0.79 | 2.2
14 | 1.069 | 2.2575 | 1.05 | 2.9 | 1.05 | 2 | 1.05 | 2 | 1.07 | 2.27 | 1.07 | 1.97 | 0.86 | 1.59 | 1.04 | 2.29 | 1.07 | 2.33 | 1.04 | 1.69 | 1.07 | 2.35 | 1.07 | 2.65 | 1.07 | 2.43 | 1.07 | 2.43 | 1.07 | 2.02 | 1.07 | 3 | 1.07 | 2.2
16 | 1.3963 | 2.2 | 1.38 | 2.69 | 1.37 | 1.8 | 1.37 | 1.8 | 1.4 | 2.27 | 1.4 | 1.94 | 1.04 | 1.61 | 1.36 | 2.29 | 1.4 | 2.33 | 1.36 | 1.54 | 1.4 | 2.34 | 1.4 | 2.51 | 1.4 | 2.89 | 1.4 | 2.89 | 1.4 | 1.12 | 1.4 | 3 | 1.4 | 2.18
18 | 1.7671 | 2.068 | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | 1.21 | 1.59 | 1.74 | 2.43 | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | 1.77 | 1.66 | 1.77 | 1.66 | n/a | n/a | 2 | 3 | n/a | n/a
19 | 1.9689 | 2.92 | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | 2.72 | 2.92 | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a
20 | 2.1817 | 1.825 | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | 1.47 | 1.61 | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | 2.18 | 1.75 | 2.18 | 1.75 | 0.78 | 2.19 | n/a | n/a | n/a | n/a
22 | 2.6398 | 2.3167 | n/a | n/a | n/a | n/a | n/a | n/a | 2.64 | 2.13 | n/a | n/a | 1.83 | 1.6 | 3.55 | 2.65 | 2.67 | 2.33 | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | 0.78 | 2.19 | 2.44 | 3 | n/a | n/a
24 | 3.1416 | 1.75 | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | 3.14 | 1.75 | 3.14 | 1.75 | n/a | n/a | n/a | n/a | n/a | n/a
26 | 3.687 | 2.57 | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | 1 | 2.57 | n/a | n/a | n/a | n/a
30 | 4.9087 | 3 | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | 3.33 | 3 | n/a | n/a
40 | 8.7266 | 2.22 | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | 2.67 | 2.22 | n/a | n/a | n/a | n/a

## New Empty Scratchpad
RAC-4096 | RAC-4112 | RAC-4128 | RAC-4144 | RAC-4160 | RAC-4166 | RAC-4170 |  | RAC-4176 |  | RAC-4192 | RAC-4208 | RAC-4224 | RAC-4240 | RAC-4256 | RAC-4272 | RAC-4288 | RAC-4304 | RAC-4311 | RAC-4320 | RAC-4336 | RAC-4352 | RAC-4368 | RAC-4384 | RAC-4400 | RAC-4416 | RAC-4432 |  | RAC-4448
v3 | [34 empty] | Manufacturer
Space Information |  |  | Network / Equipment Tree Information | [7 empty] | Network Information (MSTP and IP) | [13 empty] | Definitions and Templates |  | Sensor | Parameters
Site/Building/Floor (Required) | Room Number (Optional) | Leaf Space (e.g. Room) (Required) | Device Name (Required) | Device FQR Reference (Required) | Device Description (Optional) | Equipment Name (Required) | Mechanical Drawing | Served By Equipment Name (Optional) | JCI Ctrl Dwg No. | Controller Part # (Optional) | Engine Name (Required) | Trunk Name (Required) | Controller Host Name (Future) | JCI MAC Address | IP Controller Number | ZIGBEE PAN Offset | Instance # (BACoid) | N2Address | DHCP Enabled | IP Address | Subnet Mask | IP Router | ETH-1 (Optional) | ETH-2 (Optional) | Equipment Definition Name (Optional) | Controller Template Name (Required) | Code No | Box Heat | Supplemental Heat | Inlet Size (inches) | SA-AREA | SA-KFACTOR | CLG-MAXFLOW | CLGOCC-MINFLOW | HTGOCC-MINFLOW | Comments
|  |  | Attribute ID | [27 empty] | AV3111 | AV3112 | AV3108 | AV3109 | AV3110
|  |  | Attribute Type | [27 empty] | Default Value | Default Value | Default Value | Default Value | Default Value
Plant Systems
|  |  |  | #VALUE! | - | [11 empty] | #VALUE! | [7 empty] | CHWS | CHWS
|  |  |  | #VALUE! | - | [11 empty] | #VALUE! | [7 empty] | HWS | HWS
Air Systems
|  |  |  | #VALUE! | - | [11 empty] | #VALUE! | [7 empty] | AHU | AHU
|  |  |  | #VALUE! | - | [11 empty] | #VALUE! | [7 empty] | AHU | AHU
|  |  |  | #VALUE! | - | [11 empty] | #VALUE! | [7 empty] | AHU | AHU
Terminal Systems
|  |  |  | #VALUE! | - | [11 empty] | #VALUE! | [7 empty] | VAV | VAV-RH | NSB8BTN240-0 | TRUE | FALSE | 8 | 0.35 | 2.39 | 860 | 500 | 500
|  |  |  | #VALUE! | - | [11 empty] | #VALUE! | [7 empty] | VAV | VAV-RH | NSB8BTN240-0 | TRUE | FALSE | 7 | 0.27 | 2.57 | 550 | 350 | 350
|  |  |  | #VALUE! | - | [11 empty] | #VALUE! | [7 empty] | VAV | VAV-RH | NSB8BTN240-0 | TRUE | FALSE | 8 | 0.35 | 2.39 | 880 | 360 | 360
|  |  |  | #VALUE! | - | [11 empty] | #VALUE! | [7 empty] | VAV | VAV-RH | NSB8BTN240-0 | TRUE | FALSE | 7 | 0.27 | 2.57 | 600 | 220 | 220
|  |  |  | #VALUE! | - | [11 empty] | #VALUE! | [7 empty] | VAV | VAV-RH | NSB8BTN240-0 | TRUE | FALSE | 8 | 0.35 | 2.39 | 845 | 420 | 420
|  |  |  | #VALUE! | - | [11 empty] | #VALUE! | [7 empty] | VAV | VAV-RH | NSB8BTN240-0 | TRUE | FALSE | 5 | 0.14 | 1.95 | 350 | 150 | 150
|  |  |  | #VALUE! | - | [11 empty] | #VALUE! | [7 empty] | VAV | VAV-RH | NSB8BTN240-0 | TRUE | FALSE | 8 | 0.35 | 2.39 | 860 | 400 | 400
|  |  |  | #VALUE! | - | [11 empty] | #VALUE! | [7 empty] | VAV | VAV-RH | NSB8BTN240-0 | TRUE | FALSE | 6 | 0.2 | 3.07 | 360 | 90 | 90
|  |  |  | #VALUE! | - | [11 empty] | #VALUE! | [7 empty] | VAV | VAV-RH | NSB8BTN240-0 | TRUE | FALSE | 5 | 0.14 | 1.95 | 350 | 150 | 150
|  |  |  | #VALUE! | - | [11 empty] | #VALUE! | [7 empty] | VAV | VAV-RH | NSB8BTN240-0 | TRUE | FALSE | 5 | 0.14 | 1.95 | 280 | 80 | 80
|  |  |  | #VALUE! | - | [11 empty] | #VALUE! | [7 empty] | VAV | VAV-RH | NSB8BTN240-0 | TRUE | FALSE | 9 | 0.44 | 2.3 | 940 | 580 | 580
|  |  |  | #VALUE! | - | [11 empty] | #VALUE! | [7 empty] | VAV | VAV-RH | NSB8BTN240-0 | TRUE | FALSE | 40 | 2.67 | 2.22 | 6800 | 1900 | 1900
|  |  |  | #VALUE! | - | [11 empty] | #VALUE! | [7 empty] | VAV | VAV-RH | NSB8BTN240-0 | TRUE | FALSE | 14 | 1.07 | 2.02 | 2600 | 910 | 910
|  |  |  | #VALUE! | - | [11 empty] | #VALUE! | [7 empty] | VAV | VAV-RH | NSB8BTN240-1 | TRUE | FALSE | 8 | 0.35 | 2.39 | 750 | 400 | 400
|  |  |  | #VALUE! | - | [11 empty] | #VALUE!
|  |  |  | #VALUE! | - | [11 empty] | #VALUE!
|  |  |  | #VALUE! | - | [11 empty] | #VALUE!
|  |  |  | #VALUE! | - | [11 empty] | #VALUE!
|  |  |  | #VALUE! | - | [11 empty] | #VALUE!
|  |  |  | #VALUE! | - | [11 empty] | #VALUE!
Integrations
|  |  |  | #VALUE! | - | [11 empty] | #VALUE! | [7 empty] | VAV
|  |  |  | #VALUE! | - | [11 empty] | #VALUE! | [7 empty] | VAV
|  |  |  | #VALUE! | - | [11 empty] | #VALUE! | [7 empty] | VAV
|  |  |  | #VALUE! | - | [11 empty] | #VALUE! | [7 empty] | VAV
|  |  |  | #VALUE! | - | [11 empty] | #VALUE! | [7 empty] | VAV
|  |  |  | #VALUE! | - | [11 empty] | #VALUE! | [7 empty] | VAV

## Merge Empty Scratchpad
RAC-4096 | RAC-4112 | RAC-4128 | RAC-4144 | RAC-4160 | RAC-4166 | RAC-4170 | RAC-4176 | RAC-4192 | RAC-4208 | RAC-4224 | RAC-4240 | RAC-4256 | RAC-4272 | RAC-4288 | RAC-4304 | RAC-4311 | RAC-4320 | RAC-4336 | RAC-4352 | RAC-4368 | RAC-4384 | RAC-4400 | RAC-4416 | RAC-4432 | RAC-4448
v3
Space Information |  |  | Network / Equipment Tree Information | [5 empty] | Network Information (MSTP and IP) | [13 empty] | Definitions and Templates |  | Parameters
Site/Building/Floor (Required) | Room Number (Optional) | Leaf Space (e.g. Room) (Required) | Device Name (Provided) | Device FQR Reference (Provided) | Device Description (Provided) | Equipment Name (Required) | Served By Equipment Name (Optional) | Controller Part # (Optional) | Engine Name (Provided) | Trunk Name (Provided) | Controller Host Name (Future) | JCI MAC Address (Provided) | IP Controller Number (Provided) | ZIGBEE PAN Offset | Instance # (BACoid) (Provided) | N2Address (Provided) | DHCP Enabled (Provided) | IP Address (Provided) | Subnet Mask (Provided) | IP Router (Provided) | ETH-1 (Optional) | ETH-2 (Optional) | Equipment Definition Name (Provided) | Controller Template Name (Not Used) | SA-AREA | SA-KFACTOR | CLG-MAXFLOW | CLGOCC-MINFLOW | HTGOCC-MINFLOW
|  |  | Attribute ID | [21 empty] | AV3111 | AV3112 | AV3108 | AV3109 | AV3110
|  |  | Attribute Type | [21 empty] | Default Value | Default Value | Default Value | Default Value | Default Value

## New Site Examples
RAC-4096 | RAC-4112 | RAC-4128 | RAC-4144 | RAC-4160 | RAC-4166 | RAC-4170 | RAC-4176 | RAC-4192 | RAC-4208 | RAC-4224 | RAC-4240 | RAC-4256 | RAC-4272 | RAC-4288 | RAC-4304 | RAC-4311 | RAC-4320 | RAC-4336 | RAC-4352 | RAC-4368 | RAC-4384 | RAC-4400 | RAC-4416 | RAC-4432 | RAC-4448
v3
Space Information |  |  | All Items / Equipment Tree Information | [5 empty] | Network Information (MSTP and IP) | [13 empty] | Definitions and Templates |  | Parameters
Site/Building/Floor (Required) | Room Number (Optional) | Leaf Space (e.g. Room) (Required) | Device Name (Required) | Device FQR Reference (Required) | Device Description (Optional) | Equipment Name | Served By Equipment Name (Optional) | Controller Part # (Optional) | Engine Name (Required) | Trunk Name (Required) | Controller Host Name (Future) | JCI MAC Address | IP Controller Number | ZIGBEE PAN Offset | Instance # (BACoid) | N2Address | DHCP Enabled | IP Address | Subnet Mask | IP Router | ETH-1 (Optional) | ETH-2 (Optional) | Equipment Definition Name (Optional) | Controller Template Name (Required)
Attribute ID
Attribute Type
Central Plant Examples (MSTP Network Information) - For Central Plant Space Information, a sites campus name is typically entered under the Site/Bldg./Floor column and a Building Name entered as the Leaf Space. - For All Items / Equipment Tree Information, the Device and Equipment Names can be simple but you do have the option to create a more unique FQR Reference name so the information displayed in SMP views is more detailed. - There are typically no Served By Equipment Names for Central Plants unless the boilers, chillers, pumps etc. are created as unique Equipment instances after the Plant System Equipment is created. - Remember to setup the Point Name Display attributes in the Controller Templates to match the desired Point Naming strategy for the site. - It is reccommended that you create unique names for the Equipment and Controller Templates for Central Plants because they are typically not reused on other plant systems.
JCI University |  | Training | NCE-1-Integrated-04 | Chiller Plant |  | Chiller Plant |  | NCE | NCE-1 | Field Bus MSTP1 |  | 4 | [10 empty] | Chiller Plant-CPO-ED | Chiller Plant-CPO-CT
JCI University |  | Training | FAC-NCE-1-1-05 | Hot Water Plant |  | Hot Water Plant |  | FAC-1632 | NCE-1 | Field Bus MSTP1 |  | 5 | [10 empty] | HWS-ED | HWS-CT
Air Handling Unit Example (MSTP Network Information) - For AHU Space Information, a floor or building becomes the Leaf Space. - For All Items / Equipment Tree Information, the Device and Equipment Names can be simple but you do have the option to create a more unique FQR Reference name so the information displayed in SMP views is more detailed. - You have the option to add 1 Served By Equipment Name in the template for one of the Central Plants. Other Central Plants serving the AHUs will have to be added manaually after the Rapid Archive Process is performed. - Remember to setup the Point Name Display attributes in the Controller Template to match the desired Point Naming strategy for the site. - It is reccommended that you try to reuse a common Equipment Definition for all AHUs of the same basic Mechanical Equipment Type even if the Controller Templates / CAF Files for each AHU may be slightly different.
JCI University/Training |  | Floor 1 | FAC-NAE1-1-06-MASP | FAC-NAE1-1-06-MASP |  | AHU-MASP-1 | Chiller Plant &&Hot Water Plant | FAC-1632 | NAE-1 | Field Bus MSTP1 |  | 6 | [10 empty] | AHU-MASD-ED | AHU-MASD
JCI University/Training |  | Floor 2 | FAC-NAE1-2-06-MASP | FAC-NAE1-2-06-MASP |  | AHU-MASP-2 | Chiller Plant &&Hot Water Plant | FAC-1632 | NAE-1 | Field Bus MSTP2 |  | 6 | [10 empty] | AHU-MASD-ED | AHU-MASD
Terminal Unit Examples (MSTP Integrations) - For Terminal Unit Space Information, a Room is typically the Leaf Space. - An Optional Room Number can be added as a reference from the mechanical plans until the official Room names are known. - You have the option to add 1 Served By Equipment Name in the template. For VAV Boxes, this is typically an AHU and for Fan Coils it could be a Heating or Cooling Central Plan. Other serving relationships will have to be added manaually after the Rapid Archive Process is performed. - Remember to setup the Point Name Display attributes in the Controller Template to match the desired Point Naming strategy for the site.
JCI University/Training/Floor 1 | F1M04 | Breakout Room 01 | VAV-11-RH | VAV-11-RH |  | VAV-SD-RH-11 | AHU-MASP-1&&Chiller Plant&&Hot Water Plant | MS-VMA1630-0 | NAE-1 | Field Bus MSTP1 |  | 11 | [10 empty] | VAV Boxes - Single Duct | VAV-SD-RH | 0.769 | 2.92 | 1050 | 115 | 735
JCI University/Training/Floor 1 | F1M05 | Breakout Room 02 | VAV-12-RH | VAV-12-RH |  | VAV-SD-RH-12 | AHU-MASP-1&&Chiller Plant&&Hot Water Plant | MS-VMA1630-0 | NAE-1 | Field Bus MSTP1 |  | 12 | [10 empty] | VAV Boxes - Single Duct | VAV-SD-RH | 0.338 | 2.44 | 900 | 90 | 420
JCI University/Training/Floor 1 | F1M06 | Breakout Room 03 | VAV-13-RH | VAV-13-RH |  | VAV-SD-RH-13 | AHU-MASP-1&&Chiller Plant&&Hot Water Plant | MS-VMA1630-0 | NAE-1 | Field Bus MSTP1 |  | 13 | [10 empty] | VAV Boxes - Single Duct | VAV-SD-RH | 1.05 | 2.9 | 1540 | 135 | 1080
JCI University/Training/Floor 1 | F1M07 | Mens Bathroom | VAV-14-RH EF | VAV-14-RH EF |  | VAV-SD-RH-14 | AHU-MASP-1&&Chiller Plant&&Hot Water Plant | MS-VMA1630-0 | NAE-1 | Field Bus MSTP1 |  | 14 | [10 empty] | VAV Boxes - Single Duct | VAV-SD-RH-EF-Hum | 1.05 | 2.9 | 1600 | 130 | 1120
JCI University/Training/Floor 1 | F1M07 | Mens Bathroom | VAV-14-RH EF | VAV-14-RH EF |  | Bath EF-14 |  | MS-VMA1630-0 | NAE-1 | Field Bus MSTP1 |  | 14 | [10 empty] | Bathroom Exhuast | VAV-SD-RH-EF-Hum
JCI University/Training/Floor 1 | F1M09 | Womens Bathroom | VAV-15-RH EF | VAV-15-RH EF |  | VAV-SD-RH-EF-Hum-15 | AHU-MASP-1&&Chiller Plant&&Hot Water Plant | MS-VMA1630-0 | NAE-1 | Field Bus MSTP1 |  | 15 | [10 empty] | VAV Boxes - Single Duct | VAV-SD-RH-EF-Hum | 0.338 | 2.44 | 570 | 90 | 400
JCI University/Training/Floor 1 | F1M09 | Womens Bathroom | VAV-15-RH EF | VAV-15-RH EF |  | Bath EF-15 |  | MS-VMA1630-0 | NAE-1 | Field Bus MSTP1 |  | 15 | [10 empty] | Bathroom Exhuast | VAV-SD-RH-EF-Hum
VAV Boxes (IP Field Controllers) - For Terminal Unit Space Information, a Room is typically the Leaf Space. - An Optional Room Number can be added as a reference from the mechanical plans until the official Room names are known. - You have the option to add 1 Served By Equipment Name in the template. For VAV Boxes, this is typically an AHU and for Fan Coils it could be a Heating or Cooling Central Plan. Other serving relationships will have to be added manaually after the Rapid Archive Process is performed. - Remember to setup the Point Name Display attributes in the Controller Template to match the desired Point Naming strategy for the site.
JCI University/Training/Floor 1 | F1M01 | Electrical Closet | VAV-08-CLG | VAV-08-CLG |  | VAV-SD-CLG-08 | AHU-MASP-1&&Chiller Plant | MS-VMA1630-0 | NAE-1 | [13 empty] | VAV Boxes - Single Duct | VAV-SD-CLG | 0.532 | 2.48 | 800 | 115 | 115
JCI University/Training/Floor 1 | F1M02 | Reception | VAV-09-RH | VAV-09-RH |  | VAV-SD-RH-09 | AHU-MASP-1&&Chiller Plant&&Hot Water Plant | MS-VMA1630-0 | NAE-1 | [13 empty] | VAV Boxes - Single Duct | VAV-SD-RH | 0.769 | 2.92 | 1390 | 125 | 970
JCI University/Training/Floor 1 | F1M03 | Large Conference Room | VAV-10-RH | VAV-10-RH |  | VAV-SD-RH-10 | AHU-MASP-1&&Chiller Plant&&Hot Water Plant | MS-VMA1630-0 | NAE-1 | [13 empty] | VAV Boxes - Single Duct | VAV-SD-RH | 0.532 | 2.48 | 810 | 75 | 530
JCI University/Training/Floor 1 | F1M04 | Breakout Room 01 | VAV-11-RH | VAV-11-RH |  | VAV-SD-RH-11 | AHU-MASP-1&&Chiller Plant&&Hot Water Plant | MS-VMA1630-0 | NAE-1 | [13 empty] | VAV Boxes - Single Duct | VAV-SD-RH | 0.769 | 2.92 | 1050 | 115 | 735
JCI University/Training/Floor 1 | F1M05 | Breakout Room 02 | VAV-12-RH | VAV-12-RH |  | VAV-SD-RH-12 | AHU-MASP-1&&Chiller Plant&&Hot Water Plant | MS-VMA1630-0 | NAE-1 | [13 empty] | VAV Boxes - Single Duct | VAV-SD-RH | 0.338 | 2.44 | 900 | 90 | 420
JCI University/Training/Floor 1 | F1M06 | Breakout Room 03 | VAV-13-RH | VAV-13-RH |  | VAV-SD-RH-13 | AHU-MASP-1&&Chiller Plant&&Hot Water Plant | MS-VMA1630-0 | NAE-1 | [13 empty] | VAV Boxes - Single Duct | VAV-SD-RH | 1.05 | 2.9 | 1540 | 135 | 1080
JCI University/Training/Floor 1 | F1M07 | Mens Bathroom | VAV-14-RH EF | VAV-14-RH EF |  | VAV-SD-RH-14 | AHU-MASP-1&&Chiller Plant&&Hot Water Plant | MS-VMA1630-0 | NAE-1 | [13 empty] | VAV Boxes - Single Duct | VAV-SD-RH-EF-Hum | 1.05 | 2.9 | 1600 | 130 | 1120
JCI University/Training/Floor 1 | F1M07 | Mens Bathroom | VAV-14-RH EF | VAV-14-RH EF |  | Bath EF-14 |  | MS-VMA1630-0 | NAE-1 | [13 empty] | Bathroom Exhuast | VAV-SD-RH-EF-Hum
JCI University/Training/Floor 1 | F1M09 | Womens Bathroom | VAV-15-RH EF | VAV-15-RH EF |  | VAV-SD-RH-15 | AHU-MASP-1&&Chiller Plant&&Hot Water Plant | MS-VMA1630-0 | NAE-1 | [13 empty] | VAV Boxes - Single Duct | VAV-SD-RH-EF-Hum | 0.338 | 2.44 | 570 | 90 | 400
JCI University/Training/Floor 1 | F1M09 | Womens Bathroom | VAV-15-RH EF | VAV-15-RH EF |  | Bath EF-15 |  | MS-VMA1630-0 | NAE-1 | [13 empty] | Bathroom Exhuast | VAV-SD-RH-EF-Hum
JCI University/Training/Floor 1 | F1M11 | Classroom 01 | VAV-16-RH | VAV-16-RH |  | VAV-SD-RH-16 | AHU-MASP-1&&Chiller Plant&&Hot Water Plant | MS-VMA1630-0 | NAE-1 | [13 empty] | VAV Boxes - Single Duct | VAV-SD-RH | 1.05 | 2.9 | 1860 | 145 | 1300
JCI University/Training/Floor 1 | F1M12 | Classroom 02 | VAV-17-RH | VAV-17-RH |  | VAV-SD-RH-17 | AHU-MASP-1&&Chiller Plant&&Hot Water Plant | MS-VMA1630-0 | NAE-1 | [13 empty] | VAV Boxes - Single Duct | VAV-SD-RH | 0.769 | 2.92 | 1350 | 115 | 990
JCI University/Training/Floor 1 | F1M13 | Classroom 03 | VAV-18-RH | VAV-18-RH |  | VAV-SD-RH-18 | AHU-MASP-1&&Chiller Plant&&Hot Water Plant | MS-VMA1630-0 | NAE-1 | [13 empty] | VAV Boxes - Single Duct | VAV-SD-RH | 1.05 | 2.9 | 1650 | 125 | 1155
JCI University/Training/Floor 1 | F1M14 | Classroom 04 | VAV-19-RH | VAV-19-RH |  | VAV-SD-RH-19 | AHU-MASP-1&&Chiller Plant&&Hot Water Plant | MS-VMA1630-0 | NAE-1 | [13 empty] | VAV Boxes - Single Duct | VAV-SD-RH | 1.05 | 2.9 | 1650 | 135 | 1200
JCI University/Training/Floor 1 | F1M15 | Classroom 05 | VAV-20-RH | VAV-20-RH |  | VAV-SD-RH-20 | AHU-MASP-1&&Chiller Plant&&Hot Water Plant | MS-VMA1630-0 | NAE-1 | [13 empty] | VAV Boxes - Single Duct | VAV-SD-RH | 0.532 | 2.48 | 800 | 105 | 700
JCI University/Training/Floor 1 | F1M16 | Storage | VAV-21-CLG | VAV-21CLG |  | VAV-SD-CLG-21 | AHU-MASP-1*Chiller Plant | MS-VMA1630-0 | NAE-1 | [13 empty] | VAV Boxes - Single Duct | VAV-SD-CLG | 0.532 | 2.48 | 800 | 110 | 460
JCI University/Training/Floor 2 | F2M01 | Elevator Lobby | VAV-08-RH | VAV-08-RH |  | VAV-SD-RH-8 | AHU-MASP-1&&Chiller Plant&&Hot Water Plant | MS-VMA1630-0 | NAE-1 | [13 empty] | VAV Boxes - Single Duct | VAV-SD-RH | 1.05 | 2.9 | 1520 | 130 | 1065
JCI University/Training/Floor 2 | F2M02 | Large Conference Room | VAV-09-RH | VAV-09-RH |  | VAV-SD-RH-9 | AHU-MASP-1&&Chiller Plant&&Hot Water Plant | MS-VMA1630-0 | NAE-1 | [13 empty] | VAV Boxes - Single Duct | VAV-SD-RH | 1.05 | 2.9 | 1500 | 125 | 1050
JCI University/Training/Floor 2 | F2M03 | Breakout Room 01 | VAV-10-RH | VAV-10-RH |  | VAV-SD-RH-10 | AHU-MASP-1&&Chiller Plant&&Hot Water Plant | MS-VMA1630-0 | NAE-1 | [13 empty] | VAV Boxes - Single Duct | VAV-SD-RH | 1.375 | 2.69 | 2100 | 155 | 1400
JCI University/Training/Floor 2 | F2M03 | Multipurpose 01&&Multipurpose 02 | VAV-11-RH | VAV-11-RH |  | VAV-SD-RH-11 | AHU-MASP-1&&Chiller Plant&&Hot Water Plant | MS-VMA1630-0 | NAE-1 | [13 empty] | VAV Boxes - Single Duct | VAV-SD-RH | 1.375 | 2.69 | 2100 | 155 | 1400

## Merged Site Examples
RAC-4096 | RAC-4112 | RAC-4128 | RAC-4144 | RAC-4160 | RAC-4166 | RAC-4170 | RAC-4176 | RAC-4192 | RAC-4208 | RAC-4224 | RAC-4240 | RAC-4256 | RAC-4272 | RAC-4288 | RAC-4304 | RAC-4311 | RAC-4320 | RAC-4336 | RAC-4352 | RAC-4368 | RAC-4384 | RAC-4400 | RAC-4416 | RAC-4432 | RAC-4448
v3
Space Information |  |  | All Items / Equipment Tree Information | [5 empty] | Network Information (MSTP and IP) All Data is Provided from the Export Depending on the Integration Types | [13 empty] | Definitions and Templates |  | Parameters
Site/Building/Floor (Required) | Room Number (Optional) | Leaf Space (e.g. Room) (Required) | Device Name (Provided) | Device FQR Reference (Provided) | Device Description (Provided) | Equipment Name (Optional) | Served By Equipment Name (Optional) | Controller Part # (Optional) | Engine Name (Provided) | Trunk Name (Provided) | Controller Host Name (Future) | JCI MAC Address | IP Controller Number | ZIGBEE PAN Offset | Instance # (BACoid) | N2Address | DHCP Enabled | IP Address | Subnet Mask | IP Router | ETH-1 (Optional) | ETH-2 (Optional) | Equipment Definition Name (Required) | Controller Template Name (Not Used)
Attribute ID
Attribute Type
Central Plant Examples (MSTP Network Information) - For Central Plant Space Information, a sites campus name is typically entered under the Site/Bldg./Floor column and a Building Name entered as the Leaf Space. - For All Items / Equipment Tree Information, the Device and Equipment Names can be simple but you do have the option to create a more unique FQR Reference name so the information displayed in SMP views is more detailed. - There are typically no Served By Equipment Names for Central Plants unless the boilers, chillers, pumps etc. are created as unique Equipment instances after the Plant System Equipment is created. - Remember to setup the Point Name Display attributes in the Controller Templates to match the desired Point Naming strategy for the site. - It is reccommended that you create unique names for the Equipment and Controller Templates for Central Plants because they are typically not reused on other plant systems.
JCI University |  | Training | NCE-1-Integrated-04 | Chiller Plant |  | Chiller Plant |  | NCE | NCE-1 | Field Bus MSTP1 |  | 4 | [10 empty] | Chiller Plant-CPO-ED
JCI University |  | Training | FAC-NCE-1-1-05 | Hot Water Plant |  | Hot Water Plant |  | FAC-1632 | NCE-1 | Field Bus MSTP1 |  | 5 | [10 empty] | HWS-ED
Air Handling Unit Example (MSTP Network Information) - For AHU Space Information, a floor or building becomes the Leaf Space. - For All Items / Equipment Tree Information, the Device and Equipment Names can be simple but you do have the option to create a more unique FQR Reference name so the information displayed in SMP views is more detailed. - You have the option to add 1 Served By Equipment Name in the template for one of the Central Plants. Other Central Plants serving the AHUs will have to be added manaually after the Rapid Archive Process is performed. - Remember to setup the Point Name Display attributes in the Controller Template to match the desired Point Naming strategy for the site. - It is reccommended that you try to reuse a common Equipment Definition for all AHUs of the same basic Mechanical Equipment Type even if the Controller Templates / CAF Files for each AHU may be slightly different.
JCI University/Training |  | Floor 1 | FAC-NAE1-1-06-MASP | FAC-NAE1-1-06-MASP |  | AHU-MASP-1 | Chiller Plant &&Hot Water Plant | FAC-1632 | NAE-1 | Field Bus MSTP1 |  | 6 | [10 empty] | AHU-MASD-ED
JCI University/Training |  | Floor 2 | FAC-NAE1-2-06-MASP | FAC-NAE1-2-06-MASP |  | AHU-MASP-2 | Chiller Plant &&Hot Water Plant | FAC-1632 | NAE-1 | Field Bus MSTP2 |  | 6 | [10 empty] | AHU-MASD-ED
Terminal Unit Examples (MSTP Integrations) - For Terminal Unit Space Information, a Room is typically the Leaf Space. - An Optional Room Number can be added as a reference from the mechanical plans until the official Room names are known. - You have the option to add 1 Served By Equipment Name in the template. For VAV Boxes, this is typically an AHU and for Fan Coils it could be a Heating or Cooling Central Plan. Other serving relationships will have to be added manaually after the Rapid Archive Process is performed. - Remember to setup the Point Name Display attributes in the Controller Template to match the desired Point Naming strategy for the site.
JCI University/Training/Floor 1 | F1M04 | Breakout Room 01 | VAV-11-RH | VAV-11-RH |  | VAV-SD-RH-11 | AHU-MASP-1&&Chiller Plant&&Hot Water Plant | MS-VMA1630-0 | NAE-1 | Field Bus MSTP1 |  | 11 | [10 empty] | VAV Boxes - Single Duct
JCI University/Training/Floor 1 | F1M05 | Breakout Room 02 | VAV-12-RH | VAV-12-RH |  | VAV-SD-RH-12 | AHU-MASP-1&&Chiller Plant&&Hot Water Plant | MS-VMA1630-0 | NAE-1 | Field Bus MSTP1 |  | 12 | [10 empty] | VAV Boxes - Single Duct
JCI University/Training/Floor 1 | F1M06 | Breakout Room 03 | VAV-13-RH | VAV-13-RH |  | VAV-SD-RH-13 | AHU-MASP-1&&Chiller Plant&&Hot Water Plant | MS-VMA1630-0 | NAE-1 | Field Bus MSTP1 |  | 13 | [10 empty] | VAV Boxes - Single Duct
JCI University/Training/Floor 1 | F1M07 | Mens Bathroom | VAV-14-RH EF | VAV-14-RH EF |  | VAV-SD-RH-14 | AHU-MASP-1&&Chiller Plant&&Hot Water Plant | MS-VMA1630-0 | NAE-1 | Field Bus MSTP1 |  | 14 | [10 empty] | VAV Boxes - Single Duct
JCI University/Training/Floor 1 | F1M07 | Mens Bathroom | VAV-14-RH EF | VAV-14-RH EF |  | Bath EF-14 |  | MS-VMA1630-0 | NAE-1 | Field Bus MSTP1 |  | 14 | [10 empty] | Bathroom Exhuast
JCI University/Training/Floor 1 | F1M09 | Womens Bathroom | VAV-15-RH EF | VAV-15-RH EF |  | VAV-SD-RH-EF-Hum-15 | AHU-MASP-1&&Chiller Plant&&Hot Water Plant | MS-VMA1630-0 | NAE-1 | Field Bus MSTP1 |  | 15 | [10 empty] | VAV Boxes - Single Duct
JCI University/Training/Floor 1 | F1M09 | Womens Bathroom | VAV-15-RH EF | VAV-15-RH EF |  | Bath EF-15 |  | MS-VMA1630-0 | NAE-1 | Field Bus MSTP1 |  | 15 | [10 empty] | Bathroom Exhuast
VAV Boxes (IP Field Controllers) - For Terminal Unit Space Information, a Room is typically the Leaf Space. - An Optional Room Number can be added as a reference from the mechanical plans until the official Room names are known. - You have the option to add 1 Served By Equipment Name in the template. For VAV Boxes, this is typically an AHU and for Fan Coils it could be a Heating or Cooling Central Plan. Other serving relationships will have to be added manaually after the Rapid Archive Process is performed. - Remember to setup the Point Name Display attributes in the Controller Template to match the desired Point Naming strategy for the site.
JCI University/Training/Floor 1 | F1M01 | Electrical Closet | VAV-08-CLG | VAV-08-CLG |  | VAV-SD-CLG-08 | AHU-MASP-1&&Chiller Plant | MS-VMA1630-0 | NAE-1 | [13 empty] | VAV Boxes - Single Duct
JCI University/Training/Floor 1 | F1M02 | Reception | VAV-09-RH | VAV-09-RH |  | VAV-SD-RH-09 | AHU-MASP-1&&Chiller Plant&&Hot Water Plant | MS-VMA1630-0 | NAE-1 | [13 empty] | VAV Boxes - Single Duct
JCI University/Training/Floor 1 | F1M03 | Large Conference Room | VAV-10-RH | VAV-10-RH |  | VAV-SD-RH-10 | AHU-MASP-1&&Chiller Plant&&Hot Water Plant | MS-VMA1630-0 | NAE-1 | [13 empty] | VAV Boxes - Single Duct
JCI University/Training/Floor 1 | F1M04 | Breakout Room 01 | VAV-11-RH | VAV-11-RH |  | VAV-SD-RH-11 | AHU-MASP-1&&Chiller Plant&&Hot Water Plant | MS-VMA1630-0 | NAE-1 | [13 empty] | VAV Boxes - Single Duct
JCI University/Training/Floor 1 | F1M05 | Breakout Room 02 | VAV-12-RH | VAV-12-RH |  | VAV-SD-RH-12 | AHU-MASP-1&&Chiller Plant&&Hot Water Plant | MS-VMA1630-0 | NAE-1 | [13 empty] | VAV Boxes - Single Duct
JCI University/Training/Floor 1 | F1M06 | Breakout Room 03 | VAV-13-RH | VAV-13-RH |  | VAV-SD-RH-13 | AHU-MASP-1&&Chiller Plant&&Hot Water Plant | MS-VMA1630-0 | NAE-1 | [13 empty] | VAV Boxes - Single Duct
JCI University/Training/Floor 1 | F1M07 | Mens Bathroom | VAV-14-RH EF | VAV-14-RH EF |  | VAV-SD-RH-14 | AHU-MASP-1&&Chiller Plant&&Hot Water Plant | MS-VMA1630-0 | NAE-1 | [13 empty] | VAV Boxes - Single Duct
JCI University/Training/Floor 1 | F1M07 | Mens Bathroom | VAV-14-RH EF | VAV-14-RH EF |  | Bath EF-14 |  | MS-VMA1630-0 | NAE-1 | [13 empty] | Bathroom Exhuast
JCI University/Training/Floor 1 | F1M09 | Womens Bathroom | VAV-15-RH EF | VAV-15-RH EF |  | VAV-SD-RH-15 | AHU-MASP-1&&Chiller Plant&&Hot Water Plant | MS-VMA1630-0 | NAE-1 | [13 empty] | VAV Boxes - Single Duct
JCI University/Training/Floor 1 | F1M09 | Womens Bathroom | VAV-15-RH EF | VAV-15-RH EF |  | Bath EF-15 |  | MS-VMA1630-0 | NAE-1 | [13 empty] | Bathroom Exhuast
JCI University/Training/Floor 1 | F1M11 | Classroom 01 | VAV-16-RH | VAV-16-RH |  | VAV-SD-RH-16 | AHU-MASP-1&&Chiller Plant&&Hot Water Plant | MS-VMA1630-0 | NAE-1 | [13 empty] | VAV Boxes - Single Duct
JCI University/Training/Floor 1 | F1M12 | Classroom 02 | VAV-17-RH | VAV-17-RH |  | VAV-SD-RH-17 | AHU-MASP-1&&Chiller Plant&&Hot Water Plant | MS-VMA1630-0 | NAE-1 | [13 empty] | VAV Boxes - Single Duct
JCI University/Training/Floor 1 | F1M13 | Classroom 03 | VAV-18-RH | VAV-18-RH |  | VAV-SD-RH-18 | AHU-MASP-1&&Chiller Plant&&Hot Water Plant | MS-VMA1630-0 | NAE-1 | [13 empty] | VAV Boxes - Single Duct
JCI University/Training/Floor 1 | F1M14 | Classroom 04 | VAV-19-RH | VAV-19-RH |  | VAV-SD-RH-19 | AHU-MASP-1&&Chiller Plant&&Hot Water Plant | MS-VMA1630-0 | NAE-1 | [13 empty] | VAV Boxes - Single Duct
JCI University/Training/Floor 1 | F1M15 | Classroom 05 | VAV-20-RH | VAV-20-RH |  | VAV-SD-RH-20 | AHU-MASP-1&&Chiller Plant&&Hot Water Plant | MS-VMA1630-0 | NAE-1 | [13 empty] | VAV Boxes - Single Duct
JCI University/Training/Floor 1 | F1M16 | Storage | VAV-21-CLG | VAV-21CLG |  | VAV-SD-CLG-21 | AHU-MASP-1*Chiller Plant | MS-VMA1630-0 | NAE-1 | [13 empty] | VAV Boxes - Single Duct
JCI University/Training/Floor 2 | F2M01 | Elevator Lobby | VAV-08-RH | VAV-08-RH |  | VAV-SD-RH-8 | AHU-MASP-1&&Chiller Plant&&Hot Water Plant | MS-VMA1630-0 | NAE-1 | [13 empty] | VAV Boxes - Single Duct
JCI University/Training/Floor 2 | F2M02 | Large Conference Room | VAV-09-RH | VAV-09-RH |  | VAV-SD-RH-9 | AHU-MASP-1&&Chiller Plant&&Hot Water Plant | MS-VMA1630-0 | NAE-1 | [13 empty] | VAV Boxes - Single Duct
JCI University/Training/Floor 2 | F2M03 | Breakout Room 01 | VAV-10-RH | VAV-10-RH |  | VAV-SD-RH-10 | AHU-MASP-1&&Chiller Plant&&Hot Water Plant | MS-VMA1630-0 | NAE-1 | [13 empty] | VAV Boxes - Single Duct
JCI University/Training/Floor 2 | F2M03 | Multipurpose 01&&Multipurpose 02 | VAV-11-RH | VAV-11-RH |  | VAV-SD-RH-11 | AHU-MASP-1&&Chiller Plant&&Hot Water Plant | MS-VMA1630-0 | NAE-1 | [13 empty] | VAV Boxes - Single Duct

## VAV SD Parms
VAV Single Duct
Balancer Override SD
SA-AREA | SA-KFACTOR | CLG-MAXFLOW | CLGOCC-MINFLOW | HTGOCC-MINFLOW
AV3111 | AV3112 | AV3108 | AV3109 | AV3110
Default Value | Default Value | Default Value | Default Value | Default Value
VAV Single Duct with Exhaust
Balancer Override SDX
SA-AREA | SA-KFACTOR | CLG-MAXFLOW | CLGOCC-MINFLOW | HTGOCC-MINFLOW | EA-AREA | EA-KFACTOR | OCCEAFLOW-DIFF
AV3116 | AV3117 | AV3113 | AV3114 | AV3115 | AV3511 | AV3512 | AV3513
Default Value | Default Value | Default Value | Default Value | Default Value | Default Value | Default Value | Default Value
VAV Damper |  |  |  |  | Exhaust Damper
Integrated Actuator
DPR-O
Hardware | Hardware | Hardware
AO2131 | AO2131 | AO2131
Polarity | Effective Stroke Time | Present Value
Proportional Actuator |  |  |  |  | Proportional Actuator
DPR-O |  |  |  |  | EAD-O
Hardware | Hardware | Hardware |  |  | Hardware | Hardware | Hardware
AO2131 | AO2131 | AO2131 |  |  | AO2038 | AO2038 | AO2038
Min Out Value | Max Out Value | Present Value |  |  | Min Out Value | Max Out Value | Present Value
Incremental Actuator |  |  |  |  | Incremental Actuator
DPR-O |  |  |  |  | EAD-O
Hardware | Hardware | Hardware |  |  | Hardware | Hardware | Hardware
AO2030 | AO2030 | AO2030 |  |  | AO2040 | AO2040 | AO2040
Polarity | Effective Stroke Time | Present Value |  |  | Polarity | Effective Stroke Time | Present Value
Electric Heat
Minimum Flow Determiniation
HTG-MINFLOW
AV3268
Default Value

## VAV DD Parms
VAV Dual Duct
Balancer Override DD
CD-AREA | CD-KFACTOR | HD-AREA | HD-KFACTOR | CLG-MAXFLOW | CDOCC-MINFLOW | HTG-MAXFLOW | HDOCC-MINFLOW
AV3092 | AV3093 | AV3096 | AV3097 | AV3094 | AV3098 | AV3095 | AV3099
Default Value | Default Value | Default Value | Default Value | Default Value | Default Value | Default Value | Default Value
VAV Dual Duct with Exhaust
Balancer Override DDX
CD-AREA | CD-KFACTOR | HD-AREA | HD-KFACTOR | CLG-MAXFLOW | CDOCC-MINFLOW | HTG-MAXFLOW | HDOCC-MINFLOW | EA-AREA | EA-KFACTOR | OCCEAFLOW-DIFF
AV3100 | AV3101 | AV3104 | AV3105 | AV3102 | AV3106 | AV3103 | AV3107 | AV3508 | AV3509 | AV3510
Default Value | Default Value | Default Value | Default Value | Default Value | Default Value | Default Value | Default Value | Default Value | Default Value | Default Value
Cold Deck Damper |  |  |  | Hot Deck Damper |  |  |  | Exhaust Damper
Integrated Actuator |  |  |  | Integrated Actuator
CD-O |  |  |  | HD-O
Hardware | Hardware | Hardware |  | Hardware | Hardware | Hardware
AO2019 | AO2019 | AO2019 |  | AO2069 | AO2069 | AO2069
Polarity | Effective Stroke Time | Present Value |  | Polarity | Effective Stroke Time | Present Value
Proportional Actuator |  |  |  | Proportional Actuator |  |  |  | Proportional Actuator
CD-O |  |  |  | HD-O |  |  |  | EAD-O
Hardware | Hardware | Hardware |  | Hardware | Hardware | Hardware |  | Hardware | Hardware | Hardware
AO2018 | AO2018 | AO2018 |  | AO2068 | AO2068 | AO2068 |  | AO2038 | AO2038 | AO2038
Min Out Value | Max Out Value | Present Value |  | Min Out Value | Max Out Value | Present Value |  | Min Out Value | Max Out Value | Present Value
Incremental Actuator |  |  |  | Incremental Actuator |  |  |  | Incremental Actuator
CD-O |  |  |  | HD-O |  |  |  | EAD-O
Hardware | Hardware | Hardware |  | Hardware | Hardware | Hardware |  | Hardware | Hardware | Hardware
AO2019 | AO2019 | AO2019 |  | AO2069 | AO2069 | AO2069 |  | AO2040 | AO2040 | AO2040
Polarity | Effective Stroke Time | Present Value |  | Polarity | Effective Stroke Time | Present Value |  | Polarity | Effective Stroke Time | Present Value

## Heating Valves Parms
Box Heating Valve |  |  | Supplemental Heating Valve
Proportional Actuator |  |  | Proportional Actuator
HTG-O |  |  | SUPHTG-O
Hardware | Hardware | Hardware | Hardware | Hardware | Hardware
AO2014 | AO2014 | AO2014 | AO2127 | AO2127 | AO2127
Min Out Value | Max Out Value | Present Value | Min Out Value | Max Out Value | Present Value
Incremental Actuator |  |  | Incremental Actuator
HTG-O |  |  | SUPHTG-O
Hardware | Hardware | Hardware | Hardware | Hardware | Hardware
AO2015 | AO2015 | AO2015 | AO2129 | AO2129 | AO2129
Polarity | Effective Stroke Time | Present Value | Polarity | Effective Stroke Time | Present Value

## Misc Parms
Miscellaneous Parameters
Network Inputs/Outputs | Supply Damper Control v51
OCC-SCHEDULE | SAFLOW-SP
MV59 | AV3384
Default Value | Default Value
Supply Flow Calculation | DA-VP
SA-F | Hardware
AV3515 | AI1094
Present Value | Present Value
DA-T | ZN-T
Hardware | Hardware
AI1019 | AI1106
Present Value | Present Value

## Area & K-Factors
Anemostat
| Generic VAV Box | [11 empty] | Carnes Cross-Flow
| If you have an unknown manufacture, or the manufacturre is not listed in this sheet, use the K Factors below. | [11 empty] | Carnes Standard
VAV Box Duct Size | Area | Average K Factor | [10 empty] | Carrier
4 | 0.087266 | 1.9956 | [10 empty] | EH Price
5 | 0.13635 | 2.1564 | [10 empty] | Enviromental Tech 45
6 | 0.19635 | 2.3919 | [10 empty] | Enviromental Tech 90
7 | 0.26725 | 2.3855 | [10 empty] | Krueger
8 | 0.34907 | 2.1875 | [10 empty] | Metal Industries
9 | 0.44179 | 2.3 | [10 empty] | Nailor
10 | 0.54542 | 2.1825 | [10 empty] | Other
12 | 0.7854 | 2.3638 | [10 empty] | Redd-i
14 | 1.069 | 2.2575 | [10 empty] | Temperature Industries
16 | 1.3963 | 2.2 | [10 empty] | Tempmaster (York)
18 | 1.7671 | 2.068 | [10 empty] | Titus
19 | 1.9689 | 2.92 | [10 empty] | Tuttle and Bailey
20 | 2.1817 | 1.825 | [10 empty] | VariTrane F-Style
22 | 2.6398 | 2.3167
24 | 3.1416 | 1.75
26 | 3.687 | 2.57
30 | 4.9087 | 3
40 | 8.7266 | 2.22
| Anemostat |  | Carnes Standard |  | Carnes Cross-Flow |  | Carrier |  | EH Price SD/FP/DD Inlet Boxes |  | Environmental Tech. 45 deg travel (Largo)
VAV Box Duct Size
| Area | K Factor | Area | K Factor | Area | K Factor | Area | K Factor | Area | K Factor | Area | K Factor
4 | n/a | n/a | n/a | n/a | n/a | n/a | 0.09 | 2.26 | 0.09 | 1 | 0.09 | 1.71
5 | 0.13 | 3.28 | 0.13 | 2.42 | 0.13 | 2.42 | 0.14 | 2.26 | 0.14 | 1.47 | 0.14 | 1.69
6 | 0.19 | 2.58 | 0.19 | 2.37 | 0.19 | 2.37 | 0.2 | 2.45 | 0.2 | 2.8 | 0.2 | 1.67
7 | 0.26 | 2.85 | 0.26 | 2.4 | 0.26 | 2.4 | 0.27 | 2.27 | 0.27 | 2.34 | n/a | n/a
8 | 0.34 | 2.44 | 0.34 | 2.2 | 0.34 | 2.2 | 0.35 | 2.27 | 0.35 | 2.24 | 0.35 | 1.61
9 | 0.43 | 2.46 | n/a | n/a | n/a | n/a | 0.44 | 2.27 | 0.44 | 2.21 | n/a | n/a
10 | 0.53 | 2.48 | 0.53 | 2.1 | 0.53 | 2.1 | 0.55 | 2.27 | 0.55 | 1.96 | 0.52 | 1.63
12 | 0.77 | 2.92 | 0.77 | 2 | 0.77 | 2 | 0.79 | 2.27 | 0.79 | 2.03 | 0.69 | 1.61
14 | 1.05 | 2.9 | 1.05 | 2 | 1.05 | 2 | 1.07 | 2.27 | 1.07 | 1.97 | 0.86 | 1.59
16 | 1.38 | 2.69 | 1.37 | 1.8 | 1.37 | 1.8 | 1.4 | 2.27 | 1.4 | 1.94 | 1.04 | 1.61
18 | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | 1.21 | 1.59
19 | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a
20 | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | 1.47 | 1.61
22 | n/a | n/a | n/a | n/a | n/a | n/a | 2.64 | 2.13 | n/a | n/a | 1.83 | 1.6
24 | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a
26 | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a
30 | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a
40 | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a
| EnviroTech 90deg Travel (Largo) |  | Krueger |  | Metal Industries |  | Nailor |  | Redd-i |  | Temperature Industries
VAV Box Duct Size
| Area | K Factor | Area | K Factor | Area | K Factor | Area | K Factor | Area | K Factor | Area | K Factor
4 | 0.08 | 1.63 | 0.09 | 2.32 | n/a | n/a | 0.09 | 2.92 | n/a | n/a | n/a | n/a
5 | 0.13 | 1.66 | 0.14 | 2.31 | n/a | n/a | 0.14 | 2.99 | n/a | n/a | 0.14 | 1.62
6 | 0.18 | 2.9 | 0.2 | 2.32 | 0.18 | 1.5 | 0.2 | 3.08 | 0.2 | 2.39 | 0.2 | 1.78
7 | n/a | n/a | 0.27 | 2.32 | n/a | n/a | 0.27 | 2.85 | n/a | n/a | 0.27 | 1.62
8 | 0.33 | 2.52 | 0.35 | 2.33 | 0.33 | 1.46 | 0.35 | 2.65 | 0.35 | 2.89 | 0.35 | 1.36
9 | n/a | n/a | 0.44 | 2.33 | n/a | n/a | 0.44 | 2.23 | n/a | n/a | n/a | n/a
10 | 0.53 | 2.41 | 0.55 | 2.32 | 0.52 | 1.52 | 0.55 | 2.42 | 0.55 | 2.98 | 0.55 | 1.68
12 | 0.76 | 2.38 | 0.79 | 2.32 | 0.76 | 1.48 | 0.79 | 2.52 | 0.79 | 2.79 | 0.79 | 2.77
14 | 1.04 | 2.29 | 1.07 | 2.33 | 1.04 | 1.69 | 1.07 | 2.35 | 1.07 | 2.65 | 1.07 | 2.43
16 | 1.36 | 2.29 | 1.4 | 2.33 | 1.36 | 1.54 | 1.4 | 2.34 | 1.4 | 2.51 | 1.4 | 2.89
18 | 1.74 | 2.43 | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | 1.77 | 1.66
19 | 2.72 | 2.92 | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a
20 | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | 2.18 | 1.75
22 | 3.55 | 2.65 | 2.67 | 2.33 | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a
24 | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | 3.14 | 1.75
26 | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a
30 | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a
40 | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a
| Tempmaster (York) |  | Titus |  | Tuttle and Bailey |  | VariTrane F-Style Boxes
VAV Box Duct Size | Area | K Factor | Area | K Factor | Area | K Factor | Area | K Factor
4 | n/a | n/a | 0.09 | 1.63 | 0.09 | 2.8 | 0.09 | 1.69
5 | 0.14 | 1.62 | 0.14 | 1.95 | 0.14 | 3 | 0.14 | 1.5
6 | 0.2 | 1.78 | 0.2 | 3.07 | 0.2 | 2.9 | 0.2 | 2.31
7 | 0.27 | 1.62 | 0.27 | 2.57 | 0.27 | 3 | n/a | n/a
8 | 0.35 | 1.36 | 0.35 | 2.39 | 0.35 | 2.9 | 0.35 | 2.18
9 | n/a | n/a | 0.44 | 2.3 | n/a | n/a | n/a | n/a
10 | 0.55 | 1.68 | 0.55 | 2.31 | 0.55 | 3 | 0.55 | 2.06
12 | 0.79 | 2.77 | 0.79 | 2.76 | 0.79 | 3 | 0.79 | 2.2
14 | 1.07 | 2.43 | 1.07 | 2.02 | 1.07 | 3 | 1.07 | 2.2
16 | 1.4 | 2.89 | 1.4 | 1.12 | 1.4 | 3 | 1.4 | 2.18
18 | 1.77 | 1.66 | n/a | n/a | 2 | 3 | n/a | n/a
19 | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a
20 | 2.18 | 1.75 | 0.78 | 2.19 | n/a | n/a | n/a | n/a
22 | n/a | n/a | 0.78 | 2.19 | 2.44 | 3 | n/a | n/a
24 | 3.14 | 1.75 | n/a | n/a | n/a | n/a | n/a | n/a
26 | n/a | n/a | 1 | 2.57 | n/a | n/a | n/a | n/a
30 | n/a | n/a | n/a | n/a | 3.33 | 3 | n/a | n/a
40 | n/a | n/a | 2.67 | 2.22 | n/a | n/a | n/a | n/a